SECTION 133423

# PART 1 – GENERAL

1.01	SUMMARY

Provide all labor, equipment and materials to furnish one prefabricated  Security Guard Booth.

1.02 	Related work specified elsewhere

A.	Electrical service supply and connection.

B.	Site/foundation work.

C.	Unloading, placement, installation and anchoring.

D.	Plumbing & piping (if required).

1.3  	Submittals

- Upon award of order, manufacturer shall prepare and submit shop drawings for each different building required for this project. Drawings shall include elevations, section, floor plan, electric schedule, service entrance locations, and anchor clip detail.

1.4 	Quality assurance

- Structures shall be the product of a manufacturer with a minimum of 20 years-documented experience in the design and fabrication of portable steel buildings.

- Prefabricated buildings by manufacturers other than the one approved shall submit sufficient data to enable approval to be given. As a minimum: design drawings and/or calculations, applicable certifications, catalog information, and color samples showing equal range of variety.

- Design loads: Live Loads: Per requirements for the installation location. Unit to be manufactured to be in full compliance with the State the booth is located in.  If that State has Modular Building approval program requirements, manufacture to obtain State approval and third party inspection prior to shipping, including the State approval Insignia affixed to the booth before shipping.

# PART 2 - PRODUCTS

2.1	MANUFACTURERS

- Products of the following manufacturer from the basis for design and quality intended.

1.	B.I.G. Enterprises, Inc. South El Monte CA. 800-669-1449

B.	Or equal as approved in accordance with Section 01600 for Substitutions.

  - Structure

- Prefabricated steel building shall be single unit welded construction. Building to be shipped completely assembled. All welded joints ground smooth. Dimensions to be __’ x __’  Booth to be designed to meet U.L. 752 standards for Level 3 protection.  Booth shall have this protection in ALL areas from the finished floor height up to the finished ceiling height.  The roof, fascia, overhang, soffit and floor are not protected.  Level 3 is designed to resist attack from 3 shots from a Super Power Hand Gun such as the .44 Magnum and the like, using 240 grain SWC cartridge with a velocity range of 1350 to 1485 ft\sec.

B.	2" x 3" and 3” x 3” x .083”  where energy code compliance is required.  Framing is cold drawn electro-welded structural mechanical steel frames.

  - WALLS

A.	16ga. Galvanized steel interior walls and U.L. Level 3 armor plate steel exterior.  Walls to be insulated to R-17.

Note: Certain States require a added exterior continuous layer of minimum R 7.5 insulation encapsulated in the final layer of 16ga. galvanized steel.

  - Base and floor

A.	Unit to have a 12ga. galvanized steel plate floor welded to a 2” x 2” or 2” x 3” perimeter galvanized steel tube frame with structural galvanized steel joists welded to the frame.  Floor deck to be covered with 20” square black polyvinyl chloride interlocking tiles and a 4” black base cove.

  - Door

A.	Unit to have two commercial  steel framed insulated sliding doors top hung by eight 3” diameter rigid steel ball bearing rollers with a lower stainless steel guide, stainless steel pull handles welded to the frame, mortise lock, window and complete weather stripping.

  - Windows

A.	16ga. galvanized steel window frame system with flush mounted corners and welded fastening. Unit to have fixed windows on all sides, all windows glazed with U.L. Level 3 tined laminated glass clad polycarbonate.

  - Roof

- Roof to be a standing seam hip style designed for exterior use.  Roof to be constructed of internal steel framing that is covered with 3\4” exterior grade plywood siding and roofing paper.  Roof to be finished with 24ga. galvanized steel standing seam decking with a baked on Kynar 500 finish. Roof structure to be insulated to R-19 minimum, and shall have a 6” tall fascia with 6” overhang.  Roof to  have removable lifting eyes.

  - counter

A.	Booth to have a 2” deep full width galvanized steel at the front wall.  Shelf mounted at 34” A.F.F and painted to match the booth color.

  - Electrical

A.	Load Center shall be 125 Amp rated 120/240 volt, single phase, 3 wire 12 pole with 40 amp main breaker. Two 120V duplex outlets mounted under the shelf, LED lights recessed in a 16ga. galvanized steel ceiling with single pole wall switch, through the wall mounted air conditioner with 12,000 BTU cooling and 11,200 BTU electric heating at 230 volts.  HVAC to be mounted in a painted steel shroud.

WEATHER PROOFING

A.	Weather-tight for exterior use. All seams and joints pressure bonderized. All openings fully weather stripped. Roof shall have heat protective membrane coating.

# PART 3 - EXECUTION

  - General

A.	Install prefabricated buildings on flat and level concrete pad in accordance with the manufacturer's recommendations and placement drawings. Position units over utility stub-ups, verify building is level and anchor.

  - INSTALLATION

A.	Units shall be shipped fully assembled, fully wired, fully glazed and thoroughly painted.

- Position units over electrical stub-up on level pad. Drill and set expansion type anchor bolts.

- Connect power and seal around edges where the floor base meets the concrete pad.

END OF SECTION